## Automated
Please select correct values for yellow cells, please enter only one Ah rating. For questions please call 800-333-1194.
VOLTAGE DC |  | Number of Cells | 6AH Rating | 10AH Rating | 20AH Rating | [5 empty] | Which Pick | Type | Discharge | Bulk | Equaliz | g9 | g11 | g13 | g15 | g17 | G19
48 |  | 24 | 740 | [7 empty] | 1 | Flooded | 1.7 | 2.516 | 2.6 | 1.7 | 2.516 | 2.6 | 2.6 | 1.7 | 2.516
Select Battery Type |  | Flooded | *Enter only one AH Rating | [7 empty] | 0 | Sealed | 1.75 | 2.325 | 2.35 | 1.75 | 2.325 | 2.325 | 2.35 | 1.75 | 2.325
Battery Condition |  | Average | Enter Xtender Model |  | 93-M1007 | [5 empty] | 0 | Gel | 1.75 | 2.325 | 2.408 | 1.75 | 2.325 | 2.325 | 2.408 | 1.75 | 2.325
Using Smart Discharger? |  |  | NO | [6 empty] | 0 | 0 | AGM | 1.75 | 2.325 | 2.408 | 1.75 | 2.325 | 2.325 | 2.408 | 1.75 | 2.325
| C10 capacity | [5 empty] | 814 |  |  | 0
MODE | VOLTAGE(V) |  | CURRENT(A) |  | TIME(H) | Method | PULSE | Functional Description | TRUE | 1 | [5 empty] | G9P | G11P | G13P | G15P | G17P | G19P
MODE 1 | 40.8 |  | 81.4 |  | 10 | Discharge | 1 | Capacity Test and Activation | FALSE | 0 |  | 2.5 |  |  |  | 1.7 | 2.516 | 2.6 | 2.6 | 1.7 | 2.516
[9 empty] | FALSE | 0 |  |  |  | 2.55
MODE 2 | 60.384 |  | 81.4 |  | 10 | Restore | 7 | Restoration and Charge | sum | 1
MODE 3 | 62.4 |  | 28.49 |  | 6 | Restore | 4 | Cycle Charge/Discharge | [6 empty] | Capacity Test and Activation
Restoration and Bulk Charge (80%)
MODE 4 | 62.4 |  | 40.7 |  | 8 | Restore | 2 | Equalization |  |  |  | c10 | 81.4 |  | Restoration and Equalization
[11 empty] | 16.28 | c6 | 123.3333 |  | Restoration and Cool Down
MODE 5 | 40.8 |  | 81.4 |  | 10 | Discharge | 1 | Final Capacity Test | [6 empty] | Final Capacity Test
MODE 6 | 60.384 |  | 81.4 |  | 10 | Restore | 7 | Restoration and Charge | 40.7 | 40.7
81.4
Always use battery manufacturer recommended charging algorithm when possible! | [14 empty] | YES
61.2 | [7 empty] | 81.4 | 8 |  |  | Current Mod |  |  | NO
60 |  |  |  |  | A |  | 77 |  | 6 |  | 6 | 28.49 | 28.49 |  | 0 | G9P: Using dis?
| FALSE | [7 empty] | 4 |  | 8 | 20.35 | 20.35
0 |  |  | Average |  |  |  | Capacity Test and Activation |  | 3 |  | 8 | 12.21 | 12.21
max v cel | 62.4 |  | Below Average |  |  |  | Restoration and Charge
|  |  | Poorest |  |  |  | Equalization |  |  |  |  | 81.4 |  | C6DISC | 123.3333
| max V |  |  | Unit | CAP |  | Cycle Charge/Discharge
0 | 100 | 93-M1001 | 300 | 7 | 1322 |  | Final Capacity Test | current sDis | Unit Current C |  |  | 740 | 740
0 | 120 | 93-M1005 | 500 |  |  |  |  | 81.4 | 100 |  |  | 0 | 0
1 | 125 | 93-M1007 | 1000 |  | Selected C10 |  | Above Machine Cap? |  | Over CL? |  | C6 Calc | 0 | 0
0 | 125 | 93-M1007-480 | 1000 |  | 814 |  | 0 |  | FALSE |  |  |  | 740
0 | 75 | 93-M1009 | 3000 |  |  |  | Over 1000AH? | Percent Over |  |  | C6
|  |  |  | 1009 or 1007 |  |  | 0 | 1 |  |  | C10
Selected Vlim |  | 1009/7 and >cap |  | 1 |  |  | Additional Time |  |  |  | C20
125 |  | FALSE |  |  |  |  | 100% | Time NO dis | 10
[8 empty] | Time Dis | 6 |  | c20toc6
c10toc6
C6

## Sheet1
MODE | VOLTAGE(V) | CURRENT(A) | TIME(H) | SELECT | PULSE
MODE 1 | 1.7 x Number of Cells | C10 AH x 10% | 10:00 | DISCHARGE | 1
MODE 2 | 2.5 x Number of Cells | C10 AH x 10% | 8:00 | RESTORATION | 1
MODE 3 | 2.5 x Number of Cells | C10 AH x 5% | 8:00 | RESTORATION | 2
MODE 4 | 1.7 x Number of Cells | C10 AH x 10% | 10:00 | DISCHARGE | 1
MODE 5 | 2.5 x Number of Cells | C10 AH x 10% | 8:00 | RESTORATION | 1
MODE 6 | 2.5 x Number of Cells | C10 AH x 5% | 8:00 | RESTORATION | 2
MODE | VOLTAGE(V) | CURRENT(A) | TIME(H) | SELECT | PULSE
MODE 1 | 30.6V | 74.8A | 10:00 | DISCHARGE | 1
MODE 2 | 45V | 74.8A | 8:00 | RESTORATION | 1
MODE 3 | 45V | 37.4A | 8:00 | RESTORATION | 2
MODE 4 | 30.6V | 74.8A | 10:00 | DISCHARGE | 1
MODE 5 | 45V | 74.8A | 8:00 | RESTORATION | 1
MODE 6 | 45V | 37.4A | 8:00 | RESTORATION | 2
MODE | VOLTAGE(V) | CURRENT(A) | TIME(H) | SELECT | PULSE
MODE 1 | 1.7 x Number of Cells | C10 AH x 10% | 10:00 | DISCHARGE | 1
MODE 2 | Bulk Charge Vpc x Number of cells | C10 AH x 10% | 8:00 | RESTORATION | 1
MODE 3 | Equalization Charge Vpc x Number of cells | C10 AH x 5% | 8:00 | RESTORATION | 2
MODE 4 | 1.7 x Number of Cells | C10 AH x 10% | 10:00 | DISCHARGE | 1
MODE 5 | Bulk Charge Vpc x Number of cells | C10 AH x 10% | 8:00 | RESTORATION | 1
MODE 6 | Equalization Charge Vpc x Number of cells | C10 AH x 5% | 8:00 | RESTORATION | 2
* Vpc = Volts per Cell